## Sheet1
Voltage (kV) | Equipment | Condition | Approximate Year Installed | Approximate Age (years) | Location | Indoor/Outdoor | Notes
LIQUIDS PROCESS
13.8 | Main Switchgear (MSG) | Fair/Good | 2003/2006 | 11 | Hot House (Main electrical Building) | Indoor | Potentially impacted by CWWTP project
0.48 | Power Center PC-3 | Poor | 1967 | 47 | Boiler Building (old auxillary blower building) | Indoor | Not impacted by CWWTP Project
13.8/0.48 | Substation (Transformer T14) | Good | 2003 | 11 | East of Maintenance Center (Old Main Pump Station) | Outdoor | Not impacted by CWWTP Project | 1500 kVA | Ckt 'B-1'
0.48 | Unit Substation (480V SWGR) | Fair/Good | 2003 | 11 | East of Maintenance Center (Old Main Pump Station) | Exterior non-walk-in enclosure | Not impacted by CWWTP Project
13.8/0.48 | Substation (Transformer T15) | Fair/Good | 2003 | 11 | East of Maintenance Center (Old Main Pump Station) | Outdoor | Not impacted by CWWTP Project | 1500 kVA | Ckt 'B-2'
0.48 | Unit Substation (480V SWGR) | Good | 2003 | 11 | East of Maintenance Center (Old Main Pump Station) | Exterior non-walk-in enclosure | Not impacted by CWWTP Project
0.48 | Power Center PC-1 (Switchgear 'S6') | Poor | 1967 | 47 | Maintenance Center (Old Main Pump Station) | Indoor | Not impacted by CWWTP Project
0.48 | Switchgear ‘S5’ | Poor | 1967 | 47 | Maintenance Center (Old Main Pump Station) | Indoor | Not impacted by CWWTP Project
13.8/0.48 | Transformer T-17-1 | Fair/Good | 1998 | 16 | South grit | Outdoor | Replaceable through CWWTP Improvements project | 1000 kVA | Ckt 'C-1B'
13.8/0.48 | Transformer T-17-2 | Fair/Good | 1998 | 16 | South grit | Outdoor | Replaceable through CWWTP Improvements project | 1000 kVA | Ckt 'C-2'
13.8 | Switchgear ‘S2’ | Poor | 1979 | 35 | South of Process Center Bldg | Outdoor Load Interupter Switchgear | If it feeds south grit, replaceable; need more info on "process center" to determine what is fed
13.8/0.48 | Transformer T-9 | Poor | 1979 | 35 | South of Process Center Bldg | Outdoor | If it feeds south grit, replaceable; need more info on "process center" to determine what is fed | 1500 kVA | Ckt 'C-1B'
13.8/4.16 | Transformer T-11 | Poor | 1979 | 35 | South of Process Center Bldg | Outdoor | If it feeds south grit, replaceable; need more info on "process center" to determine what is fed | 2500 kVA | Ckt 'C-1B'
13.8 | Switchgear ‘S3’ | Poor | 1979 | 35 | South of Process Center Bldg | Outdoor Load Interupter Switchgear | If it feeds south grit, replaceable; need more info on "process center" to determine what is fed
13.8/0.48 | Transformer T-10 | Poor | 1979 | 35 | South of Process Center Bldg | Outdoor | If it feeds south grit, replaceable; need more info on "process center" to determine what is fed | 1500 kVA | Ckt 'C-2'
13.8/4.16 | Transformer T-12 | Poor | 1979 | 35 | South of Process Center Bldg | Outdoor | If it feeds south grit, replaceable; need more info on "process center" to determine what is fed | 2500 kVA | Ckt 'C-2'
0.48 | Unit Substation 'U7' | Poor | 1979 | 35 | Process Center First Floor | Indoor | If it feeds south grit, replaceable; need more info on "process center" to determine what is fed | Ckt 'C-1B/C-2'
13.8 | Pad Mounnt SWGR | Good | 2003 | 11 | Operations Center | Pad Mounted Outdoor Switchgear | If it feeds south grit, replaceable; need more info on "process center" to determine what is fed | Ckt 'C-1'
13.8/0.48 | Transformer T-13 | Poor | 1984 | 30 | Operations Center | Outdoor | If it feeds south grit, replaceable; need more info on "process center" to determine what is fed | 1000 kVA | Ckt 'C-1A'
4.16 | MV Starter Panel 'M1' | Poor | 1979 | 35 | Process center First floor | Indoor | If it feeds south grit, replaceable; need more info on "process center" to determine what is fed
4.16 | Blower Starters (Sync) | Good | 1994 | 20 | Process center First floor | Indoor | Replaceable through CWWTP Improvements project
13.8 | 13.8kV Load Interupter Switchgear | Fair | 2003 | 11 | Blower Building | Exterior non-walk-in enclosure | Replaceable through CWWTP Improvements project | Ckt 'D-1/D-2'
13.8/0.48 | Transformer T-13-1 | Fair | 1993 | 21 | Blower Building | Outdoor | Replaceable through CWWTP Improvements project | 2000 kVA | Ckt 'D-1A'
13.8/0.48 | Transformer T-13-2 | Fair | 1993 | 21 | Blower Building | Outdoor | Replaceable through CWWTP Improvements project | 2000 kVA | Ckt 'D-2A'
13.8/4.16 | Transformer T-13-3 | Fair | 1993 | 21 | Blower Building | Outdoor | Replaceable through CWWTP Improvements project | 5000 kVA | Ckt 'D-1A'
13.8/4.16 | Transformer T-13-4 | Fair | 1993 | 21 | Blower Building | Outdoor | Replaceable through CWWTP Improvements project | 5000 kVA | Ckt 'D-2A'
13.8/0.48 | Transformer T-4-1 | Fair | 1993 | 21 | North Aeration Tanks | Outdoor | Replaceable through CWWTP Improvements project | 1500 kVA | Ckt 'D-1B'
13.8/0.48 | Transformer T-4-2 | Fair | 1993 | 21 | North Aeration Tanks | Outdoor | Replaceable through CWWTP Improvements project | 1500 kVA | Ckt 'D-2B'
4.16 | MVMCC-H1 31 | Good | 1994 | 20 | Blower Building | Indoor | Replaceable through CWWTP Improvements project | Ckt 'D-1A'
4.16 | MVMCC-H1 32 | Good | 1994 | 20 | Blower Building | Indoor | Replaceable through CWWTP Improvements project | Ckt 'D-2A'
13.8/0.48 | Unit Substation 'U1' (Transformer T1) | Poor | 1979 | 35 | West Side of Thickening Building | Outdoor | METRO Currently replacing/removing | 750 kVA | Ckt 'E-1
13.8/0.48 | Unit Substation 'U1' (Transformer T2) | Poor | 1979 | 35 | West Side of Thickening Building | Outdoor | METRO Currently replacing/removing | 750 kVA | Ckt 'E-2'
0.48 | Unit Substation 'U1' (480V SWGR) | Poor | 1979 | 35 | West Side of Thickening Building | Exterior walk-in enclosure | METRO Currently replacing/removing | Ckt 'E-1/E-2A'
13.8/0.48 | Unit Substation 'U2' ((Transformer T3) | Fair | 1992 | 22 | North of Secondary Settling Tanks | Outdoor | Replaceable through CWWTP Improvements project | 1000 kVA | Ckt 'E-1/E-2A'
13.8/0.48 | Unit Substation 'U2' ((Transformer T4) | Fair | 1992 | 22 | North of Secondary Settling Tanks | Outdoor | Replaceable through CWWTP Improvements project | 1000 kVA | Ckt 'E-1/E-2A'
0.48 | Unit Substation 'U2' (480V SWGR) | Fair | 1992 | 22 | North of Secondary Settling Tanks | Exterior walk-in enclosure | Replaceable through CWWTP Improvements project | Ckt 'E-1/E-2A'
13.8/0.48 | Unit Substation 'U3' (Transformer T5) | Poor | 1979 | 35 | East of Aeration Control Room | Outdoor | Replaceable through CWWTP Improvements project | 2500 kVA | Ckt 'E-1/E-2A'
13.8/0.48 | Unit Substation 'U4' (Transformer T6) | Poor | 1979 | 35 | East of Aeration Control Room | Outdoor | Replaceable through CWWTP Improvements project | 2500 kVA | Ckt 'E-1/E-2'
0.48 | Unit Substation 'U8' (480V SWGR) | Poor | 1980 | 34 | East of Aeration Control Room | Exterior walk-in enclosure | Replaceable through CWWTP Improvements project
13.8/0.48 | Unit Substation 'U5' (Transformer T7) | Poor | 1979 | 35 | East of Aeration Control Room | Outdoor | Replaceable through CWWTP Improvements project | 2500 kVA | Ckt 'E-1/E-2A'
13.8/0.48 | Unit Substation 'U6' (Transformer T8) | Fair | 1995 | 19 | East of Aeration Control Room | Outdoor | Replaceable through CWWTP Improvements project | 2500 kVA | Ckt 'E-1/E-2A'
0.48 | Unit Substation 'U9' (480V SWGR) | Poor | 1980 | 34 | East of Aeration Control Room | Exterior walk-in enclosure | Replaceable through CWWTP Improvements project
13.8/0.48 | Transformer 06AT-1 | Good | 1993 | 21 | Bio-Odor Control Building | Padmount | Replaceable through CWWTP Improvements project | 1500 kVA | Ckt 'C-1'
13.8/0.48 | Transformer T5-1 | Fair | 1993 | 21 | North Return Sludge Building | Outdoor | Replaceable through CWWTP Improvements project | 1500 kVA | Ckt 'E-1'
13.8/0.48 | Transformer T5-2 | Fair | 1993 | 21 | North Return Sludge Building | Outdoor | Replaceable through CWWTP Improvements project | 1500 kVA | Ckt 'E-2'
13.8/0.48 | Transformer T15-1 | Fair (*) | 1993 | 21 | Chlor/De-Chlorination Building | Outdoor | Replaceable through CWWTP Improvements project | 300 kVA | Ckt 'E-1'
13.8/0.48 | Transformer T15-2 | Fair (*) | 1993 | 21 | Chlor/De-Chlorination Building | Outdoor | Replaceable through CWWTP Improvements project | 300 kVA | Ckt 'E-2B' | (Fed from 'E-2' via pad mount swgr)
13.8/0.48 | Transformer 15T-1 | Transformer has been removed |  |  | Effluent PS/Chlorine Contact Chamber | Padmount |  | 300 kVA | Ckt 'E-1' | Relocated to new chlorine site
13.8/0.48 | Transformer 15T-2 | Fair (*) | 1993 | 21 | Effluent PS/Chlorine Contact Chamber | Padmount | Replaceable through CWWTP Improvements project | 300 kVA | Ckt 'E-1' | To be relocated to new chlorine site (Dec. 2014)
13.8/4.16 | Transformer 18T-1 | Fair/Good | 1996 | 18 | Central Pumping Station | Outdoor | Replaceable through CWWTP Improvements project | 5000 kVA | Ckt 'F-1'
13.8/4.16 | Transformer 18T-2 | Fair/Good | 1996 | 18 | Central Pumping Station | Outdoor | Replaceable through CWWTP Improvements project | 5000 kVA | Ckt 'F-2'
13.8/0.48 | Transformer 18T-3 | Fair/Good | 1996 | 18 | Central Pumping Station | Outdoor | Replaceable through CWWTP Improvements project | 750 kVA | Ckt 'F-2'
13.8/0.48 | Transformer 18T-4 | Fair/Good | 1996 | 18 | Central Pumping Station | Outdoor | Replaceable through CWWTP Improvements project | 750 kVA | Ckt 'F-1'
4.16 | MVSB-181 | Good | 1999 | 15 | Central Pumping Station | Indoor | Replaceable through CWWTP Improvements project | Ckt 'F-1/F-2'
0.48 | MCC-P1-1 (MCC-1) | Poor | 1967 | 47 | Maintenance Center (Old Main Pump Station) | Indoor | Not impacted by CWWTP Project
0.48 | MCC-P1-2 | Poor | 1967 | 47 | Maintenance Center (Old Main Pump Station) | Indoor | Not impacted by CWWTP Project
0.48 | 11MCC-1 | Good | 2009 | 5 | Sludge Transfer Control Building | Indoor | Potentially impacted by CWWTP project
0.48 | 11MCC-2 | Good | 2009 | 5 | Sludge Transfer Control Building | Indoor | Potentially impacted by CWWTP project
0.48 | MCC-P2 | Poor | 1979 | 35 | South of Filter Bldg | Indoor | METRO Currently replacing/removing
0.48 | MCC-P3-1 (MCC-3) | Poor | 1957 | 57 | Old Sedinemntation Building | Indoor | Not impacted by CWWTP Project
0.48 | MCC-P3-2 | Poor | 1957 | 57 | South Aeration Pipe Gallery (old main PS pipe gallery) | Indoor | Not impacted by CWWTP Project
0.48 | MCC-P4 (Front Gate MCC) | Poor | 1967 | 47 | Coarse Bar Screen | Indoor | Replaceable through CWWTP Improvements project
0.48 | MCC-P6 | Good | 2013 | 2 | South Primary Treatment Building #1 | Indoor | Potentially impacted by CWWTP project
0.48 | MCC-P21 | Poor | 1979 | 35 | Sludge transfer Control Building | Indoor | METRO Currently replacing/removing
0.48 | MCC-P111 | Poor | 1979 | 35 | Sludge transfer Control Building | Indoor | METRO Currently replacing/removing
0.48 | MCC-101 (MCC-1) | Poor | 1957 | 57 | Maintenance Center (Old Main Pump Station) | Indoor | Not impacted by CWWTP Project
0.48 | MCC-P8 | Poor | 1979 | 35 | Boiler Building (old auxillary blower building) | Indoor | Not impacted by CWWTP Project
0.48 | MCC-P171 | Good | 1998 | 16 | South grit | Indoor | Potentially impacted by CWWTP project
0.48 | MCC-P172 | Good | 1998 | 16 | South grit | Indoor | Potentially impacted by CWWTP project
0.48 | MCC-P18-A | Good | 1996 | 18 | Central Pumping Station | Indoor | Potentially impacted by CWWTP project
0.48 | MCC-P18-B | Good | 1996 | 18 | Central Pumping Station | Indoor | Potentially impacted by CWWTP project
0.48 | MCC-P91 | Poor | 1980 | 34 | Operations Center | Indoor | Need to know what these feed B-4 I can determine impact
0.48 | Panel 9E | Poor | 1980 | 34 | Operations Center | Indoor | Need to know what these feed B-4 I can determine impact
0.48 | Unit Substation U7 (480V SWGR) | Poor | 1980 | 34 | Process Center 1st Floor | Indoor | Need to know what these feed B-4 I can determine impact
0.48 | MCC-P71 | Poor | 1980 | 34 | Process Center 1st Floor | Indoor | Need to know what these feed B-4 I can determine impact
0.48 | MCC-P72 | Poor | 1980 | 34 | Process Center 1st Floor | Indoor | Need to know what these feed B-4 I can determine impact
0.48 | MCC-P73 | Poor | 1980 | 34 | Process Center 1st Floor | Indoor | Need to know what these feed B-4 I can determine impact
0.48 | MCC-P74 | Poor | 1980 | 34 | Process Center 1st Floor | Indoor | Need to know what these feed B-4 I can determine impact
0.48 | MCC-P75 | Fair/Good | 1994 | 20 | Process Center 1st Floor | Indoor | Need to know what these feed B-4 I can determine impact
0.48 | MCC-P49 | Fair | 1994 | 20 | North Aeration Tanks (Elect. Room) | Indoor | Replaceable through CWWTP Improvements project
0.48 | MCC-P410 | Fair | 1994 | 20 | North Aeration Tanks (Elect. Room) | Indoor | Replaceable through CWWTP Improvements project
0.48 | MCC-P62 | Poor | 1994 | 20 | South of Filter Bldg | Indoor | Not impacted by CWWTP Project
0.48 | MCC-P131 | Good | 1994 | 20 | Blower Building | Indoor | Replaceable through CWWTP Improvements project
0.48 | MCC-P132 | Good | 1994 | 20 | Blower Building | Indoor | Replaceable through CWWTP Improvements project
0.48 | MCC-P133 | Good | 1994 | 20 | Blower Building | Indoor | Replaceable through CWWTP Improvements project
0.48 | MCC-P134 | Good | 1994 | 20 | Blower Building | Indoor | Replaceable through CWWTP Improvements project
0.48 | MCC-P31 | Fair | 2001 | 13 | South Primary Treatment Building #3 | Indoor | Replaceable through CWWTP Improvements project
0.48 | MCC-P47 | Poor | 1980 | 34 | North of Secondary Setlling Tanks | Indoor | Replaceable through CWWTP Improvements project
0.48 | MCC-P48 | Poor | 1980 | 34 | North of Secondary Setlling Tanks | Indoor | Replaceable through CWWTP Improvements project
0.48 | MCC-P51 | Poor | 1980 | 34 | North of Secondary Setlling Tanks | Indoor | Replaceable through CWWTP Improvements project
0.48 | MCC-P52 | Poor | 1980 | 34 | North of Secondary Setlling Tanks | Indoor | Replaceable through CWWTP Improvements project
0.48 | MCC-P41 | Poor | 1980 | 34 | East of Aeration Control Room | Indoor | Replaceable through CWWTP Improvements project
0.48 | MCC-P42 | Good | 2014 | 1 | East of Aeration Control Room | Indoor | METRO Currently replacing w/VFD MCC
0.48 | MCC-P43 | Poor | 1980 | 34 | East of Aeration Control Room | Indoor | Replaceable through CWWTP Improvements project
0.48 | MCC-P44 | Poor | 1980 | 34 | East of Aeration Control Room | Indoor | Replaceable through CWWTP Improvements project
0.48 | MCC-P45 | Poor | 1980 | 34 | East of Aeration Control Room | Indoor | Replaceable through CWWTP Improvements project
0.48 | MCC-P46 | Poor | 1980 | 34 | East of Aeration Control Room | Indoor | Replaceable through CWWTP Improvements project
0.48 | MCC-P53 | Good | 1994 | 20 | North Return Sludge Building | Indoor | Replaceable through CWWTP Improvements project
0.48 | MCC-P54 | Good | 1994 | 20 | North Return Sludge Building | Indoor | Replaceable through CWWTP Improvements project
0.48 | MCC-P151 | Fair (*) | 1993 | 21 | Chlorination/Dechlorination Building | Indoor | Replaceable through CWWTP Improvements project
0.48 | MCC-P152 | Fair (*) | 1993 | 21 | Chlorination/Dechlorination Building | Indoor | Replaceable through CWWTP Improvements project
0.48 | 06AFD 1A | Good | 2012 | 2 | Bio-Odor Control Building | Indoor | Potentially impacted by CWWTP project
0.48 | 06AFD 1B | Good | 2012 | 2 | Bio-Odor Control Building | Indoor | Potentially impacted by CWWTP project
0.48 | 06MCC 1 | Good | 2012 | 2 | Bio-Odor Control Building | Indoor | Potentially impacted by CWWTP project
0.48 | DP31A | Good | 2000 | 14 | South Primary Treatment Building #2 | Indoor | Potentially impacted by CWWTP project
0.48 | DP31B | Good | 2000 | 14 | South Primary Treatment Building #2 | Indoor | Potentially impacted by CWWTP project
0.48 | 15AFD 1 | Good | 2012 | 2 | Effluent PS/Chlorine Contact Chamber | Indoor (walk-in power house) | Potentially impacted by CWWTP project
0.48 | 15AFD 2 | Good | 2012 | 2 | Effluent PS/Chlorine Contact Chamber | Indoor (walk-in power house) | Potentially impacted by CWWTP project
24.9259
BIO SOLIDS AREA
13.8 | 35 PMG 1 | Good (*) | 2009 | 5 | Bio Solids | Outdoor | May have been flooded (2010) | Ckt 'G-1/G-2'
13.8 | 45 PMG 1 | Good (*) | 2009 | 5 | Bio Solids | Outdoor | May have been flooded (2010) | Ckt 'G-1/G-2'
13.8 | 60 MVSGR 1 | Good (*) | 2009 | 5 | Bio Solids | Outdoor | May have been flooded (2010) | Ckt 'G-1/G-2'
13.8/0.48 | Transformer 35 T1 | Good (*) | 2009 | 5 | Bio Solids | Outdoor | May have been flooded (2010) | 3000 kVA | Ckt 'G-1/G-2'
13.8/0.48 | Transformer 35 T2 | Good (*) | 2009 | 5 | Bio Solids | Outdoor | May have been flooded (2010) | 3000 kVA | Ckt 'G-1/G-2'
13.8/0.48 | Transformer 45 T1 | Good (*) | 2009 | 5 | Bio Solids | Outdoor | May have been flooded (2010) | 1500 kVA | Ckt 'G-1/G-2'
13.8/0.48 | Transformer 45 T2 | Good (*) | 2009 | 5 | Bio Solids | Outdoor | May have been flooded (2010) | 1500 kVA | Ckt 'G-1/G-2'
13.8/0.48 | Transformer 60 T1 | Good (*) | 2009 | 5 | Bio Solids | Outdoor | May have been flooded (2010) | 3000 kVA | Ckt 'G-1/G-2'
13.8/0.48 | Transformer 60 T2 | Good (*) | 2009 | 5 | Bio Solids | Outdoor | May have been flooded (2010) | 3000 kVA | Ckt 'G-1/G-2'
13.8/0.48 | Transformer 60 T1 | Good (*) | 2009 | 5 | Bio Solids | Outdoor | May have been flooded (2010) | 3000 kVA | Ckt 'G-1/G-2'
13.8/0.48 | Transformer 60 T2 | Good (*) | 2009 | 5 | Bio Solids | Outdoor | May have been flooded (2010) | 3000 kVA | Ckt 'G-1/G-2'
0.48 | 35 SWGR 1 | Good (*) | 2009 | 5 | Bio Solids | Outdoor | May have been flooded (2010)
0.48 | 45 SWGR 1 | Good (*) | 2009 | 5 | Bio Solids | Outdoor | May have been flooded (2010)
0.48 | 60 SWGR 1 | Good (*) | 2009 | 5 | Bio Solids | Outdoor | May have been flooded (2010)
0.48 | 60 SWGR 2 | Good (*) | 2009 | 5 | Bio Solids | Outdoor | May have been flooded (2010)
0.48 | 35 MCC 1 | Good (*) | 2009 | 5 | Bio Solids | Indoor | May have been flooded (2010)
0.48 | 35 MCC 2 | Good (*) | 2009 | 5 | Bio Solids | Indoor | May have been flooded (2010)
0.48 | 35 MCC 3 | Good (*) | 2009 | 5 | Bio Solids | Indoor | May have been flooded (2010)
0.48 | 35 MCC 4 | Good (*) | 2009 | 5 | Bio Solids | Indoor | May have been flooded (2010)
0.48 | 45 MCC 1 | Good (*) | 2009 | 5 | Bio Solids | Indoor | May have been flooded (2010)
0.48 | 45 MCC 2 | Good (*) | 2009 | 5 | Bio Solids | Indoor | May have been flooded (2010)
0.48 | 45 DP 1 | Good (*) | 2009 | 5 | Bio Solids | Indoor | May have been flooded (2010)
0.48 | 45 DP 2 | Good (*) | 2009 | 5 | Bio Solids | Indoor | May have been flooded (2010)
0.48 | 60 MCC 1 | Good (*) | 2009 | 5 | Bio Solids | Indoor | May have been flooded (2010)
0.48 | 60 MCC 2 | Good (*) | 2009 | 5 | Bio Solids | Indoor | May have been flooded (2010)
0.48 | 60 MCC 3 | Good (*) | 2009 | 5 | Bio Solids | Indoor | May have been flooded (2010)
0.48 | 60 MCC 4 | Good (*) | 2009 | 5 | Bio Solids | Indoor | May have been flooded (2010)
0.48 | 60 MCC 5 | Good (*) | 2009 | 5 | Bio Solids | Indoor | May have been flooded (2010)
0.48 | 60 MCC 6 | Good (*) | 2009 | 5 | Bio Solids | Indoor | May have been flooded (2010)
0.48 | 50 DP 1 | Good (*) | 2009 | 5 | Bio Solids | Indoor | May have been flooded (2010)
(*) Equipment may have been damaged during the 2010 flood